## Lichtenburg project plan
DESCRIPTION | HOURS | START DATE | COMPLETION DATE | STATUS | COMMENTS
WITBANK STORES
ERI test team travel to Witbank stores | 10 | 02/08/2023 | 02/08/2023
Electrical testing transformer
Transformer team travel to Witbank stores
Place impact recorder on the transformer and note time and the date
Inspect the transformer for any missing or damaged parts and check oil level
Partially drain oil from transformer just below main cover into a clean empty tank
Dismantle the transformer for transportation | 10 | 03/08/2023 | 03/08/2023
Load the transformer onto the truck using the mobile crane
DC insulation resistance test the transformer while on the truck
Load the transformer parts onto the truck
Clear site
LICHTENBURG SUBSTATION |  |  |  |  | Eskom to remove the overhead lines and the jumpers
Transformer team travel to Lichtenburg substation | 8 | 04/08/2023 | 04/08/2023
Transformer team dismantle the faulty transformer
DC insulation resistance test the spare transformer prior offloading | 12 | 05/08/2023 | 05/08/2023
Exchange the transformer using the mobile crane
Transport the faulty transformer and the parts to ERI
DC insulation resistance test the spare transformer when is on the final position
Assemble the spare transformer
Top up the transformer with the original oil | 8 | 06/08/2023 | 06/08/2023
Bleed the transformer on all the relevant points
Remove impact recorder note time and date
Hand over the unit to Eskom and clear site
Perform Final electrical test | 12 | 07/08/2023 | 07/08/2023