**NATIONAL ASSEMBLY**

**QUESTION: 2992**

**FOR WRITTEN REPLY**

**DATE OF PUBLICATION IN INTERNAL QUESTION PAPER: 23 MAY 2025**

**(INTERNAL QUESTION PAPER NO. 22)**

**Mrs M O Clarke (DA) to ask the Minister of Health:**

(1) What (a) total number of health facilities were damaged due to natural disasters such as storms and floods in each province (i) in the 2023-24 and 2024-25 financial years and (ii) since 1 April 2025 up to the latest date for which information is available, (b) is the (aa) name of each damaged facility and (bb) total cost of the damage at each facility and (c) are the details of the damage at each facility in each specified period;

(2) (a) at which facilities have repairs been completed and what was the date of completion, (b) what is the timeline for completion at facilities where repairs are yet to be completed and (c) in what way did his department ensure that the correct supply chain and tender processes were followed at each facility when appointing contractors for repairs? **NW3451E**

**REPLY:**

1. and (2) (a)-(b)

The table below reflects on the list of facilities affected by rain damages in 2023-24 and 2024-25 as reported by six provinces. The Free State and Northern Cape Province have reported no damages, whilst we are still waiting for the report from Mpumalanga. There are 142 facilities in seven provinces affected by rain damages (including Mpumalanga) between 2023-24 and 2024-25 Financial years. The names, cost, timelines, and details scope of work per facility are reflected in the table below. The MP budget is divided equally per facility because they procured materials in bulk and give them to the artisans to repair the damages.

| **Province** | **Name of the facility** | **2023/24**  **damage?** | **2024/25**  **Damage?** | **Details of the Damage** | **Cost of the damage** | **Work start date** | **Work end date** |
| --- | --- | --- | --- | --- | --- | --- | --- |
| LP | Mphahlele Clinic | No | Yes | Replacement of trusses, corrugated iron and minor painting of ceilings damaged by rains. | R362 467.35 | 01/10/2024 | 28/02/2025 |
| LP | Van Velden Hospital | No | Yes | Repair of hospital boundary fence | R171 679.60 | 01/10/2024 | 28/02/2025 |
| LP | Ooghoek Clinic | No | Yes | Tree fell and damage roof at nurses home | R50 000.00 | 01/10/2024 | 28/02/2025 |
| LP | Jamela Clinic | No | Yes | Tree fell and damage roof at nurses home | R50 000.00 | 01/10/2024 | 28/02/2025 |
| LP | Musina Hospital | No | Yes | Details to replace 30 meters of palisade fence | R50 000.00 | 01/10/2024 | 28/02/2025 |
| LP | Olifanshoek Clinic | No | Yes | Replacement of fisher boards | R50 000.00 | 01/10/2024 | 28/02/2025 |
| LP | Nancefield Clinic | No | Yes | Replacement of gate | R20 000.00 | 01/10/2024 | 28/02/2025 |
| LP | Mutiti Clinic | No | Yes | Replacement of trusses, Corrugated iron, replacement of electricity wires | R50 000.00 | 01/10/2024 | 28/02/2025 |
| LP | Matlala Hospital | No | Yes | Installation of ceilings, painting, window glasses, walls in patches, Internal walls plaster. | R1 107 790.60 | 01/10/2024 | 28/02/2025 |
| LP | Matshageng Clinic | No | Yes | Construct a stormwater drainage in front of the gate | R50 000.00 | 01/10/2024 | 28/02/2025 |
| LP | Vlakplaats Clinic | No | Yes | Construct a stormwater drainage in front of the gate, Repair of Window, Glasses, Ceiling, Outdoor Units & Rebuild Carports | R50 000.00 | 01/10/2024 | 28/02/2025 |
| LP | Groblersdal Hospital | No | Yes | Asset stores redesign and Refurbishment, Steel structure cover Gate & repair of storm damaged  Infrastructure | R2 230 816.51 | 01/10/2024 | 30/06/2025 |
| **LP** | **Total = 12** |  |  |  | **R4 242 754.06** |  |  |
| EC | Beacon Bay Clinic | No | Yes | External: Roof leaks, gutters, and downpipes | R9 521 338.00 | Waiting for the budget | Waiting for the budget |
| EC | Chris Hani Clinic | No | Yes | Roof: remove and replace damaged galvanized mild steel roof sheets and repair roof leaks. | R7 809 000.00 | Waiting for the budget | Waiting for the budget |
| EC | Frere Gateway Clinic | No | Yes | Make good all roof fittings(gutters, downpipes, eaves) | R8 709 133.00 | Waiting for the budget | Waiting for the budget |
| EC | Gompo B Clinic | No | Yes | Roof: remove and replace damaged galvanized mild steel roof sheets and repair roof leaks. | R9 101 700.00 | Waiting for the budget | Waiting for the budget |
| EC | Gonubie Clinic | No | Yes | Replace damaged asbestos sheets and repair roof leaks. Remove from site any asbestos material in compliance with OHS requirements. | R8 616 100.00 | Waiting for the budget | Waiting for the budget |
| EC | John Dube Clinic | No | Yes | Make good all roof fittings(gutters, downpipes, eaves) | R7 153 783.00 | Waiting for the budget | Waiting for the budget |
| EC | Needs Camp Clinic | No | Yes | Roof: Remove and replace damaged concrete roof tiles and repair roof leaks. | R16 429 625.00 | Waiting for the budget | Waiting for the budget |
| EC | Open Shaw Clinic | No | Yes | Make good all roof fittings(gutters, downpipes, eaves) | R5 638 865.00 | Waiting for the budget | Waiting for the budget |
| EC | Pefferville Clinic | No | Yes | Roof: Remove and replace damaged concrete roof tiles and repair roof leaks. | R11 005 055.00 | Waiting for the budget | Waiting for the budget |
| EC | Zanempilo Clinic | No | Yes | Make good all roof fittings(gutters, downpipes, eaves) | R8 052 150.00 | Waiting for the budget | Waiting for the budget |
| EC | Willowmore Hospital | No | Yes | Roof: remove and replace damaged galvanized mild steel roof sheets and repair roof leaks. | R21 051 301.00 | Waiting for the budget | Waiting for the budget |
| EC | Victoria Hospital | No | Yes | Make good all roof fittings(gutters, downpipes, eaves) | R11 806 838.00 | Waiting for the budget | Waiting for the budget |
| EC | Canzibe Hospital | No | Yes | Roof: remove and replace damaged galvanized mild steel roof sheets and repair roof leaks. | R2 694 205.13 | Waiting for the budget | Waiting for the budget |
| EC | Isilimela Hospital | No | Yes | Make good all roof fittings (gutters, downpipes, eaves) | R3 270 729.04 | Waiting for the budget | Waiting for the budget |
| EC | Ngangelizwe CHC | No | Yes | Roof: remove and replace damaged galvanized mild steel roof sheets and repair roof leaks. | R203 241.25 | Waiting for the budget | Waiting for the budget |
| EC | Qobo Clinic | No | Yes | Make good all roof fittings (gutters, downpipes, eaves) | R492 376 | Waiting for the budget | Waiting for the budget |
| EC | Mpindweni Clinic | No | Yes | Roof: Repair waterproofing layer and provide new torch on waterproofing to roof and repaint with reflective paint. | R449 000.00 | Waiting for the budget | Waiting for the budget |
| **EC** | **TOTAL =17** |  |  |  | **R128 317 334.38** |  |  |
| GP | KT Motubatse Clinic | Yes | No | Damaged roofs, water proofing , ceilings, and painting. | R 3 165 621.10 | 03/01/2023 | 31/03/2024 |
| GP | Odi Hospital | Yes | No | Damaged roofs, ceilings, storm water drainage system, floors/vinyl, gutters & down pipes | R 4 957 609.64 | 03/01/2023 | 31/03/2024 |
| GP | Sedilega Clinic | Yes | No | Damaged sewer pipeline, storm water drainage system, ceilings | R 5 632 029.41 | 03/01/2023 | 31/03/2024 |
| GP | Block TT Clinic | Yes | No | Damaged sewer pipeline, storm water drainage system, ceilings | R 2 843 586.60 | 03/01/2023 | 31/03/2024 |
| **GP** | **TOTAL = 4** |  |  |  | **R16 598 846.75** |  |  |
| KZN | Addington Hospital | Yes | No | Addington Hospital - Repairs to flood damage at Pharmacy, MOPD & Gateway Clinic | R29,809,326 | 31/01/2027 | 31/06/2027 |
| KZN | eThekwini Infrastructure Hub | Yes | No | eThekwini Infrastructure Hub: Flood Damage Recovery-October 2023 | R2,500,000 | 01/11/2027 | 31/03/2028 |
| KZN | King Dinuzulu Hospital | Yes | No | King Dinuzulu Hospital - Flood Damage Repairs | R3,417,156 | 12/09/2024 | 21/01/2025 |
| KZN | Ngwelezane Hospital | Yes | No | Ngwelezane Hospital: Storm Damage Recovery to Doctors Residence | 1,934,097.24 | 19/06/2024 | 31/11/2025 |
| KZN | Ngwelezane Hospital | Yes | No | Ngwelezane Hospital: Storm Damage Recovery to various buildings | 333,4032.85 | 20/06/2024 | 04/06/2025 |
| KZN | Queen Nandi Regional Hospital (formerly LUMH) | Yes | No | Queen Nandi Hospital: Storm Damage Recovery | R2,200,000 | 14/03/2025 | 20/09/2025 |
| KZN | Hillcrest Hospital | No | Yes | Hillcrest Hospital: Flood Damage 2025 | R1,000,000 | 20/06/2025 | 30/09/2025 |
| KZN | KZN Childrens Hospital | No | Yes | KZN Children's Hospital - Flood Damage Recovery 2025 | R1,000,000 | 26/06/2025 | 30/09/2025 |
| KZN | Montebello Hospital | No | Yes | Montebello Hospital - Flood Damage Recovery 2025 | R3,000,000 | 17/04/2025 | 30/07/2025 |
| KZN | Ntabeni Clinic | No | Yes | Ntabeni Clinic - Flood Damage Recovery 2025 | R900,000 | 16/07/2025 | 30/11/2025 |
| KZN | Untunjambili Hospital | No | Yes | Ntunjambili Hospital - Flood Damage Recovery 2025 | R3,000,000 | 09/05/2025 | 30/09/2025 |
| KZN | Wentworth EMS Station | No | Yes | Wentworth EMS - Flood Damage Recovery | R1,000,000 | 22/07/2025 | 30/11/2025 |
| KZN | Wentworth Hospital | No | Yes | Wentworth Hospital - Flood Damage Recovery | R20,701,530 | 02/09/2024 | 31/07/2025 |
| KZN | Ekuphumuleni Clinic | No | Yes | Ekuphumuleni Clinic - Storm Damage Recovery 2024 Roof Repairs & Associated Works | R6,700,000 | 01/09/2025 | 30/05/2026 |
| KZN | Harry Gwala Regional Hospital | No | Yes | Harry Gwala Regional Hospital - Storm Damage Recovery 2024 Roof Repairs & Associated Works | R3,500,000 | 01/09/2025 | 30/03/2026 |
| KZN | Limit Hill Clinic | No | Yes | Limit Hill Clinic - Storm Damage Recovery 2024 Roof & Associated Works | R4,079,332 | 25/03/2025 | 25/06/2025 |
| **KZN** | **Total = 16** |  |  |  | **R88,075,474.09** |  |  |
| NW | Kromkuil Clinic | No | Yes | Interruption of flow of service as a results of damming of water within the premises from outside the facility.  Damaged roof and exterior wall | R450 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | JB Marks CHC | No | Yes | Interruption of flow of service as a results of damming of water within the premises from outside the facility.  Damaged Ceilings and electrical power points resulting in temporary closure of the Facility for a day | R670 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Boikhutso Clinic | No | Yes | Interruption of flow of service as a results of damming of water within the premises from outside the facility.  Damaged roof and exterior wall | R100 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Ventersdorp EMRS Station | No | Yes | Leaking roof leading to damaged Ceiling in the passage and rest rooms | R50000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Steve Tshwete Clinic | No | Yes | Leaking roof leading to damaged Ceiling of the Mother and Child Consulting Rooms | R50 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Maquasie, Kgakala, Jouberton, Tigane and RB Nzima Clinics | No | Yes | Leaking roofs of facilities due to maintenance without any damages and disruptions to services | R350 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | General De Larey Hospital | No | Yes | Interruption of service that led to temporarily closure of the facility.  Roof repairs and associated works  Buildings Completed and work in progress for external drainage | R8 000 000 | 15/01/2025 | 30/4/2025 |
| NW | Lehurutshe Hospital | No | Yes | Regional Hospital - Storm Damage Recovery 2025 Roof Repairs & Associated Works. | R4 000 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Setlopo clinic | No | Yes | Water flooded the main entrance compromising access. | R100 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Ditlhakong clinic | No | Yes | Water flooded the main entrance compromising access. | R100 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Tsetse Clinic | No | Yes | Roof leakages leading flooded consulting rooms temporarily interrupting | R100 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Ntswelesoku Health Post | No | Yes | Water flooded the entrance of the facility thus prevent entrance. | R100 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Witrand Specialized | No | Yes | Regional Hospital - Storm Damage Recovery 2025 Roof Repairs & Associated Works for entire building that requires refurbishment as building is over 100 years | R100 000 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Job Shimankana Tabane Mental Health Unit | No | Yes | Regional Hospital - Storm Damage Recovery 2025 Roof Repairs & Associated Works | R2 500 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Bapong CHC | No | yes | Interruption of flow of service as a results of damming of water within the premises from outside the facility. | R4 000 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Mafikeng Provincial Hospital | No | Yes | Roof leakages due to heavy rains affecting Casualty, Theatre, Neuro Surgeon Unit, X-Ray OPD, ward 2, 7, Records, Pharmacy, Kitchen Mortuary and Laundry temporarily affecting patients | R4 000 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Lesetlheng clinic | No | Yes | Roof leakages leading flooded consulting rooms temporarily interrupting | R300 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Phalane Clinic | No | yes | Roof leakages leading flooded consulting rooms temporarily interrupting | R300 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Moses Kotane Hospital | No | Yes | Regional Hospital - Storm Drainage blockage leading to water flowing into the Maternity Section thus disrupting services 2025, Leaking Roof Repairs & Associated Works | R4 500 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Tshepong Hospital | Yes | Yes | Storm drainage Roof leakages due to heavy rains affecting Medical Dispensary,Records, Administration Block, Casualty, Theatre, NICU, X-Ray OPD, ward 1, 2, 9, Renal, Pharmacy, Kitchen Mortuary and Laundry temporarily affecting patients | R5 000 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Khunotswane Clinic | No | Yes | Roof leakages leading flooded consulting rooms temporarily interrupting services | R300 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Lincwe Clinic | No | Yes | Replacement of trusses, corrugated iron and minor painting of ceilings damaged by rains. | R400 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Seolong Clinic | No | Yes | Roof leakages leading flooded consulting rooms temporarily interrupting services | R500 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Brakkuil Clinic | No | Yes | Roof leakages leading flooded consulting rooms temporarily interrupting services | R300 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Letlhakeng Clinic | No | Yes | Roof leakages leading flooded consulting rooms temporarily interrupting services | R300 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | David Katnagel Clinic | No | Yes | Roof leakages leading flooded consulting rooms temporarily interrupting services | R100 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Welgeval Clinic | No | Yes | Roof leakages leading flooded consulting rooms temporarily interrupting services | R100 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Koedoesrand Clinic | No | Yes | Roof leakages leading flooded consulting rooms temporarily interrupting services | R100 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | JST Hospital Mental Health Unit | Yes | Yes | Regional Hospital - Storm Damage Recovery 2025 Roof Repairs & Associated Works | R1 500 00 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| NW | Koster Hospital | Yes | Yes | Regional Hospital - Storm Damage Recovery 2025 Roof Repairs & Associated Works | R1 350 000 | Awaiting Budget Allocation | Awaiting Budget Allocation |
| **NW** | **TOTAL = 30** |  |  |  | **R40 620 000** |  |  |
| WC | Overberg District Office | Yes | No | Extreme rainy weather conditions caused damage to the roof of the Overberg district office main building as well as the prefab building and finance building. This caused the rainwater to leak in and drip inside the building and posed a danger of causing damage to equipment. | R8,494.75 |  | 3/1/2023 |
| WC | Tygerberg Boiler House | Yes | No | One of the boiler house roof sheets directly above the main DB came loose during the strong winds. With opening the wind can blow off further roof sheets. If it starts to rain, then boilers cannot be operated, because power to Boiler House main DB will have to be switched off | R4,776.86 |  | 3/14/2023 |
| WC | Toekomsrus Clinic | Yes | No | Heavy rains and wind caused roof tile damage at Toekomsrus clinic. Broken roof tiles need repair to ensure the roof is watertight. Various ceiling panels were damaged in the process. The ceiling boards need replacement. Electrical reticulation assessed and repaired. | R46,123.63 |  | 6/12/2023 |
| WC | Red Cross War Memorial Childrens Hospital | Yes | No | Roadways and walkways are flooded with recent rainfall. Main stormwater line to property boundary on west side appears to be blocked and causing flooding in several places. | R69,595.13 |  | 6/21/2023 |
| WC | Caledon Ambulance Station | Yes | No | The capping of the ambulance station has blown off during the night onto the parking area and heavy rain is expected today in Caledon. We are trying to prevent more damage to the building. Due to the darkness the staff cannot assess if there is any other damage as well. | R25,336.99 |  | 8/4/2023 |
| WC | Overberg District Office | Yes | No | The storm damaged the roof causing rain to get inside the main building. water is dripping/ leaking in 5 offices as well as the men's toilet. A large area gets wet when it rains. | R20,015.84 |  | 8/22/2023 |
| WC | Booth Memorial Step Down Facility | Yes | No | Ward 301 (2x bed ward) and Ward 310 (5x bed ward) closed due to a severe leaking roof after storm weather. The section of the roof needing waterproofing will only be reachable using scaffolding, | R412,834.48 |  | 9/27/2023 |
| WC | Worcester Hospital | Yes | No | The strong wind on Wednesday 20 September ripped the ridging off of the D2 Neonatal ward roof. Due to strong wind and rain, we could not have it fixed sooner. | R29,858.60 |  | 9/27/2023 |
| WC | Railton Clinic | Yes | No | the 2 earth leakages in Railton clinic keeps on tripping and some aircons after it has rained due to the cables being run underneath the prefab building that makes the services to run slow in the clinic | R126,010.48 |  | 10/13/2023 |
| WC | District Six CDC | Yes | No | District Six CDC roof leaking and causing flooding at the Emergency Centre and damage to the ceiling panels. This is an emergency situation, and urgent repairs need to be done to the roof as it is a risk to patients' lives, the public, and the staff. The leak in the EC, impacts if patients are being Resuscitated in Trauma. | R22,769.93 |  | 2/28/2024 |
| WC | New Somerset Hospital | Yes | No | As a result of the storm over the weekend, there are a couple of old asbestos roof plates that have been severely damaged and thus leaving large holes in the roofs of both the 5th floor in the West Wing and the Bulk Store. | R29,620.26 |  | 8/25/2023 |
| WC | Vredendal Hospital | Yes | No | Vredendal area experienced strong winds on the afternoon of 12th December 2023. It caused two dry pine trees to fall over (collapsed). These fallen trees are blocking access and are causing a safety hazard for people and vehicles.   A third dry tree is unrooted and supported by other trees from collapsing. Immediate danger. | R5,750.00 |  | 12/20/2023 |
| WC | Booth Memorial Step Down Facility | No | Yes | The windstorm on Sunday 21 January 2024 caused serious damage to the roof. Sadly the roof was repaired only a few months ago. Large sheets were blown off and other loose sheets were removed for safety's sake, | R464,619.39 |  | 2/23/2024 |
| WC | Khayelitsha Hospital | No | Yes | The ridging and gutters of various areas of KDH had blown off and parts hanging causing danger to passersby. This happened during the heavy winds we have had over the last few days and may cause danger to patients and staff in and around the hospital. | R12,335.53 |  | 4/8/2024 |
| WC | Lentegeur Boiler House | No | Yes | It was reported by security personnel that due to strong winds, the roof plate and capping came loose on the laundry and boiler room roof. Temporary repairs as first step and inclusion in project done in 2025 | R276580.15 |  | 3/18/2024 |
| WC | Helderberg Hospital | No | Yes | Due to extreme weather on 06 & 07/04/2024, some areas in the facility got badly damaged due to falling trees on roofing structures and blocked roads to facility access area. Extreme winds caused window blowouts. The items were requested by Mrs. S Leo to Mr. Badenhorst for Emergency delegation to be approved. | R44,991.52 |  | 4/12/2024 |
| WC | Tulbagh Clinic | No | Yes | The storm lifted the roof of the Tulbagh clinic. The ceiling was damaged because it was raining. All roof sheets are damaged. We need to repair the roof immediately. before the next rainfall. | R59,630.74 |  | 6/13/2024 |
| WC | Gustrouw CDC | No | Yes | With strong winds and rain in the Helderberg area, it was reported that the roof at Gustrouw CDC has been damaged. On investigation it was found that the Big six roof plates, ridging, barge boards and capping over the TB area have been broken and damaged. | R56,011.43 |  | 4/23/2024 |
| WC | Overberg District Office | No | Yes | The storm damaged the roof causing rain to get inside the main building. Water leaking into offices as well as men's toilets. rain causing damage to wooden floors and ceiling boards. Temporary repairs were done but project for replacement of the roof and repair of waterproofing is currently on site | R2,038,198.19 |  | 4/19/2024 |
| WC | Protea Park CDC | No | Yes | Protea Park CDC roof is leaking and causing the ceiling in the main patient waiting area to become loose at the ends and sulking of the ceiling. This is an emergency situation, and urgent repairs need to be done to the roof to prevent damage to the building and also to have a safe area for staff and patients. Due to the leaking roof, it is dangerous for patients to be in the main waiting area and patients have to be vacated from the area. There is a risk of the ceiling collapse, and the ceiling looks very unsafe and could drop down onto staff at any given time.  Due to the roof leaking at Protea Park Pharmacy, the following risks are present, risks to staff and patients. Risk to patients, risk to service delivery, and risk to equipment, including electrical equipment, and infrastructure. | R48,998.94 |  | 6/10/2024 |
| WC | Bongolethu Clinic | No | Yes | Multiple roof leaks on a corrugated sink roof at Bongolethu. Recently strong winds and heavy rain caused damage to the roof. Al roof nails need inspection and possible replacement. Previous attempts to seal the roof with lap and pap have perished and are full of cracks. Currently, water leaks are affecting service delivery in multiple sections of the clinic. | R22,312.94 |  | 7/18/2024 |
| WC | Retreat CHC | No | Yes | perimeter wall collapse - serious security risk to staff and patients - Facility located in a red zone. Security services will expose if perimeter wall is not repaired as soon as possible as this is a 24hour facility Trauma and MOU | R392,785.67 |  | 9/27/2024 |
| WC | Valkenberg Hospital | No | Yes | At our maximum ward 20, due to the heavy rainfall we have, the asbestos roof in the Dining area has started leaking in multiple spots. This has created significant water damage and poses a risk to both patients and staff. As a result, we need to move patients temporarily during mealtimes to ensure their safety and comfort while they are having their meals. | R25,982.92 |  | 8/18/2024 |
| WC | Ladysmith Ambulance Station | No | Yes | The roof tiles of EMS building in Ladysmith have been blown off due to strong winds in the area. Holes in roof tiles can lead to other damage, such as rain damage. It needs to be repaired before the rain comes. | R8,027.00 |  | 7/16/2024 |
| WC | New Somerset Hospital | No | Yes | Box gutters are overflowing into the roof above the 5th floor and EC in the West Block. Please arrange for core drilling toward the outside to aid the egress of the water. Please repair 5 floors expansion joints that have deteriorated to an extent that the water just runs down. Please supply expansion joint cover-plates on repaired joints. | R222,950.37 |  | 8/18/2024 |
| WC | False Bay Hospital | No | Yes | Due to the flooding of current heavy rains and storms, the False Bay Hospital grounds have been flooded preventing access to the gas bank for the delivery of any kind; this includes Afrox. | R39,257.05 |  | 7/31/2024 |
| WC | New Somerset Hospital | No | Yes | Box gutters are overflowing into the roof above the 5th floor and EC in the West Block. Please arrange for core drilling toward the outside to aid the egress of the water. Please repair 5 floors expansion joints that have deteriorated to an extent that the water just runs down. Please supply expansion joint cover-plates on repaired joints. | R264,568.54 |  | 10/22/2024 |
| WC | Gugulethu CHC | No | Yes | Due to heavy wind and rain, the roofs at the facility have been damaged. Broken asbestos plates and gutters were detected for assessment. Ventilation stags came loose from the roof and have to be repositioned and sealed again. | R42,098.63 |  | 10/14/2024 |
| WC | Vredenburg FPL | No | Yes | Due to the rainy conditions, the roof started to leak. Water dripping from the ceiling into the offices. The lights breakers have been switched off for electrical issues. | R29,115.15 |  | 9/23/2024 |
| WC | Mitchells Plain CHC | No | Yes | Due to severe weather storms in the province, the roof in the facility is leaking and disrupting essential services within the facility. Roof repaired however it just a temporally fix as the roof structure is beyond repairs | R387,215.90 |  | 8/5/2024 |
| WC | Grassy Park CDC | No | Yes | Water leaking into the Pharmacy through the concrete roof structure. Medication compromised and safety of pharmacy staff at risk due to wet floor. Additionally electrical plug points saturated with water. Due to the storm still predicted over the weekend, repairs are needed urgently. | R10,132.46 |  | 7/30/2024 |
| WC | Brooklyn Chest Hospital | No | Yes | A piece of capping was blown off, leaving a big gap on the roof which can cause a lot of damage to the ceiling and furniture inside the building. Onsite staff cannot climb to repair it because the asbestos that the roof is made of is very brittle. | R22,905.52 |  | 8/19/2024 |
| WC | Brooklyn Chest Hospital | No | Yes | With the recent rains we saw several leaks in our pharmacy. Other leaks were in the storeroom where there was valuable stock and another one just above the sewer. | R25,900.12 |  | 8/19/2024 |
| WC | District Six CDC | No | Yes | Due to the latest storm, the leak has worsened. The roof leaks are almost throughout the entire facility. It is affecting medical services with disruptions more than often. Patients are seated in these unfavorable conditions and damage to ceiling boards throughout the facility has been reported. | R44,850.72 |  | 9/25/2024 |
| WC | Ceres Hospital | No | Yes | Storm in ceres damage bella vista clinic  Roof is damaged. Water is running into the clinic. Ceilings are damaged. The tree has fallen over. Fascia boards has broken off | R40,492.03 |  | 8/29/2024 |
| WC | Erica Hostel | No | Yes | assess and repair roof at erica residence at A Block second floor. Roof blown off due to heavy winds. Needs to be repaired urgently as this is a student residential . . | R3,133.43 |  | 8/15/2024 |
| WC | Kayamandi Clinic | No | Yes | Please assist with the outside porch roof as the strong wind blew off a section of the roof outside the clinic. Please assist with the repairs. This is the request submitted by the facility regarding the outside porch roof. On assessment, it was found that the roof was fastened on the existing roof trusses. Due to the strong wind the roof got blown off and broke the existing roof trusses. half the roof hanging on the ground. | R137,225.41 |  | 11/15/2024 |
| WC | Amalienstein Clinic | No | Yes | During the storm we had over the past day it was observed that the ceiling in Amaliensteins Clinic is starting to show signs of water damage. Upon inspection of the roof, it was noticed that water was leaking in through the entire NOCK area in the middle of the roof, as well as the Gabel side area on the north side along the side. This has damaged the ceiling as well. | R9,963.00 |  | 11/26/2024 |
| WC | New Horizon Clinic | No | Yes | Due to the heavy rain, we had the clinic dispensary and entrance to clinic get a lot of water through the ceiling and patient and staff can slip and fall so | R35,673.60 |  | 11/21/2024 |
| WC | Kranshoek Clinic | No | Yes | Due to the heavy rain, we had the roof is leaking into the consultation room and passage it affecting the service delivery and also damage to building | R39,420.10 |  | 11/26/2024 |
| WC | Caledon Hospital | No | Yes | Heavy rains and leaks caused damage to the ceiling boards in the Maternity ward and the passage between the theatre and General ward. Replace The entrance door at MOU. The door has disintegrated and is hanging on one hinge, which could fall off. The ceiling board is soaked and could fall. | R128,999.46 |  | 12/5/2024 |
| WC | Nomzamo CDC | No | Yes | Tying down of roof structure and general building maintenance as wind caused damage to the structure. | R1,583,094.14 |  | 3/17/2025 |
| WC | Vredenburg EMS | No | Yes | Roof damages with strong winds and due to asbestos roof, replacement was required. | R1,106,182.62 |  | 3/31/2025 |
| WC | Vredenburg Hospital | No | Yes | In areas of the hospital the wind force rainwater through windows and roof structure. Cleaning, sealing and painting of roofs, repairing of damaged rainwater goods, sealing leaking window frames | R3,021,245.60 |  | 3/31/2025 |
| WC | Alexandra Hospital | No | Yes | Roof cover blown off on several buildings and project to be incorporated into upgrade project for repairs | R4,000,000 | 23/06/2025 |  |
| WC | Bishop Lavis CDC | No | Yes | Roof leaks experience heavy rain and strong winds. Asbestos roof and waterproofing replacement for Eastern and Southern building identified as crucial | R3,221,466.40 | 10/09/2025 |  |
| WC | Tygerberg Boilerhouse | No | Yes | The roof covers were blown away during heavy winds and rain. Included in the project for urgent roof replacement as it impacts the electrical distribution. | R464,898.89 |  | 11/25/2024 |
| **WC** | **TOTAL-47** |  |  |  | **R19,090,480.51** |  |  |

NB. Some of the facilities cost more than the rain damages because the provinces took advantage of the repair on storm damage to renovate some parts of the facilities which deteriorated because of aging and not necessarily rain damage.

To ensure that the proper procurement processes are followed, all provinces are required to follow the infrastructure procurement process as stipulated on their Supply Chain guidelines, Infrastructure Delivery Management System (IDMS) and Framework for Infrastructure Delivery and Procurement Management (FIDPM).

END.